## Slide 1
Maintenance program in the cooling circuit. DW case
Juan José Manotas
Engineering Division

## Slide 2
Computerized Maintenance Management Syst.
  For the maintenance management the commercial software PRISMA 3 has been selected as the adequate CMMS (Computerized Maintenance Management System). Functions:
  Installation description implemented in 6 levels: Facility, Building, Zone, Installation, Asset (main) and Element (part of Asset)
Software PRISMA 3
  3 Sections

## Slide 3: Work Order Example
Wide spectra of information can be specified. Manpower and technical information specifications (Drawings, technical instructions, safety instructions, tools,… )
Asset
Requester
WO number
Stock Items
Man Power

## Slide 4
Tools
Regulation
Range Document: GABC example
Range code
Specialization
Work Procedure Example

## Slide 5: Work Order generated by schedule (Preventive and Corrective Maintenance)
Worker 1
Worker 2
Worker 3
Worker 4
Outsourced Service 1
Outsourced Service 2
Outsourced Service 3
Outsourced Service 4
Internal and Outsourced services schedule
  Worker assignment
  Outsourced Service assignment
  Dates
  Work Load
  Available

## Slide 6: Work order feedback tool
Feedback by Worker:
Every day worker make report for every work order assigned.
Explain the main operations and change the type of work to finish (99) if is the case.
Manpower work time is filled with other many information.
  Workday loaded
  Few Fields to complete

## Slide 7: Work Order Measurement
Work order is generated to measure criticals points in the installation. That are not yet automated.
  Ex.: Operation to adquired the data.
  Meter
More tha 8300 measures (with many meters) in differents equipments was done.
  7 years of measurements

## Slide 8: Work Order generated by indicator
Work order generated by indicator:
Planning launch work order to clean exchanger secondary side.
Differential pressure 0.60 bar > 0.54 bar, cleaning is required
  Value to trigger Work Order
  Inictial Value (if was necesary)
  Trend
  Predicted date
  Measurer

## Slide 9: Spare parts
Spare parts Main Information
(2013-2018):
Different Families: 1.849 (bearings, filters, screw, seals, etc)
Quantity of items: 24.310
StoreShelf (positions): 3.666
StockMov: 15.920
  Managed by Prisma3 (CMMS).
  Stocks Work Flow
  Take Item and WO register
  Around 80.000 €/ last years

## Slide 10: Maintenance Key figures
Assets: 3800
Preventive Work Order: 49.909
Corrective Work Order: 13.885
Total Work Orders: 63.794
Planning Task simulated: 183.401
Number of Measurements performed: 8.321 (assets measure)
A total of 3830 Assets
  Since launched application, (2012)
  Planning Task Target
  Work Type Group

## Slide 11: Work Type Reported Graphic (time)
All figures are since we launched application, (gen-2012)
Work Group types:
  PR: Preventive+Predictive
  CR: Corrective
  CO: Conductive
  NL: Legal Operations
  ME: Improvements
  NI: New Facilities
  FO: Training
  PR: Preventive, Predictive
  Maintenance
  CR: Corrective Maintenance
  11.000 hours/year = 6 technicians
  NL: Legal Operations
  Maintenance
  (preventive also)

## Slide 12: Water Cooling Systems Pumps
Water Cooling Systems and Distribution (4 circuits)
  Hot water at 50±0,5ºC used for comfort air conditioning.
  Cold Water at 7±0,5ºC, used mainly for HVAC (air conditioning) and cooling
  Deionized water at 23±0,2ºC, to refrigerate science equipment's and accelerator rings.
  Cooling towers for chillers and Free-Cooling.
CW and HVAC Storage Tank 19 m3
DW Storage Tank 40 m3
DW Exchanger
CW and HVAC Exchanger

## Slide 13: Water Pumps
64 Main Pumps of different sizes
  Deionized Water Pumps 23ºC
  Hot Water Pumps 50ºC
  Cooling Tower Water Pumps 25ºC
  Cooling Production
  Water Pumps 7ºC
  HVAC and Cooling Water Pumps 7ºC
Some pumps pictures from differents areas

## Slide 14: Pumps Predictive Maintenance
  Data collection at 10 Points of measure:
  Horizontal, Vertical and Axial in each pump
  Displacement, Velocity
  Acceleration
  Vibration Analysis Report
Reference Standard Severity ISO 10816
  Position of accelerometers

## Slide 15: Pumps Predictive Maintenance
Results Pumps Vibration Analysis
  Measurement on more than 60 Pumps
  Report of 6 years of measures
  .
  .
  .
  Degree of Severity:
  Red: Bad
  Green: Good
  Number of measure Pumps

## Slide 16: Equipment type cost
Major costs by type of equipment:
ELECT: Electric Motor and Pump
CLIMA: Heat, Ventilation and Air Conditioning, HVAC
TURVE: Turbine Extraction and Impulsion
TRAGU: Water treatments
etc…
  The higher cost: PUMPS

## Slide 17: Deionized Water Pumps Case
  3 pumps in the same bench
  2 pumps in the same bench
12 Deionized water pumps
  Service Area: 3 Pumps (2 working + 1 backup)
  Booster Ring: 2 Pumps (1 working + 1 backup)
  Storage Ring: 3 Pumps (2 working + 1 backup)
  Experimental Hall: 2 Pumps (1 working + 1 backup)

## Slide 18: Deionized Water Pumps Case
  The maintenance costs were growing until 2015
Maintenance Cost (only in 12 Deionized Water Pumps)
  ¡We had a problem with DW Pumps!
  Corrective
  Maintenance 2012-2018
  Only 2015
  Corrective
  Maintenance 2015
  ¡Too much recurrent unexpected reparations!

## Slide 19: Deionized Water Pumps Case
  Only 2-3 months between big repairs!!!
  ¡Yes, we had a problem with DW Pumps!
Meanwhile the time between repairs was decreasing

## Slide 20: Deionized Water Pumps Case
Differents Problems:
  Bearing damage
  Misaligned
  Misaligned
  Many and repetitive problems
  CMMS: Prisma3, allowed us to analyze, identify and categorize the problems
  Year
  Lost of oil

## Slide 21: Deionized Water Pumps Case
The diagnosis and more questions:
  Predictive Analysis: Very high velocity values for pump size and type. Maintained in time.
  High Severity value ISO
  Velocity: (8 mm/sg)
  Usual values always higher than worse severity ISO
  From P10A pump
  Consequently, high values occur in acceleration also and finally damage.
  What about harmonic excitations?
  The design of the bench is the best to avoid them?
  What about of the rigidity of the bench (deformation amplitudes)?

## Slide 22
  Fundamental frequencies and harmonics
  We had the need to study the solution
  Bench simulation to discover natural frequencies in different vibration modes shapes.
Deionized Water Pumps Case
Simulation, design, construction and test: New design of the bench
Mode | Simulated [Hz] | Measured [Hz]
f0 | 4 | 8,45
f1 | 55,1 | 59,92
f2 | 55,8 | 74,25
f 3 | 127,5 | 125,1
f 4 | 128,8 | 129,1
  Modes shapes summary

## Slide 23
Deionized Water Pumps Case
  Steel Base empty: f0=121 Hz
  Steel Base fill (steel): f0=168 Hz
Push the resonance modes to higher frequencies far away of the harmonic
  Dynamic Electro-pump loads coinciding with a natural frequency, can cause resonance, the design looking for push this frequencies far away the natural ones and his harmonics.

## Slide 24
Deionized Water Pumps Case
Applied solutions
  Split the slab in two independent one for each pumping group.
  Concrete thick base
  Steel base plate
Steel plate
Perimeter Steel
frame
Isolation Pad
Concrete-steel gluing
Concrete
Top/bottom steel frame
L steel profile
  Proposed Design

## Slide 25
Deionized Water Pumps Case
Construction and Test
  Frame
  Shaker final test
  Complete Frame ended
  Concrete Filling
  30 days of concrete setting

## Slide 26
Deionized Water Pumps Case
Installation and commissioning
  Moving the slab
  Cutting the concrete
  Done

## Slide 27
Deionized Water Pumps Case
Installation and commissioning
  Final position
  Moving the slab
  New one
  Waiting the New slab

## Slide 28
Deionized Water Pumps Case
Installation and commissioning
  The next…
  12 Pumps moving….dozens of tons

## Slide 29
Deionized Water Pumps Case
The results were as expected
  2015 New slabs installation
  The corrective in the pumps has dropped between 50% - 60%
  - 3 %
Impact of total cost of all maintenance
Corrective is going down

## Slide 30
This exercise it has been a very good example of how interact and work all together the multidisciplinary profiles of our engineers at CELLS Engineering Division.
Technician and Engineers from several fields such us Infrastructure, Workshop, Maintenance technicians, Civil Works, Survey&Alignment, Project Office, Draftsmen, Designers and Calculists.
Deionized Water Pumps Case
Conclusions
  After 7 year in operation the Engineering Division is working on the upgrade of their Maintenance Program.
  According to our infrastructure growth the number of equipment pieces will increase.
  New installation will be included on the Maintenance Program: Radio Frequency (RF) Plants at Service Area, Beam Lines, and Helium Plant.

## Slide 31
Thank you.