## Slide 2: Magnet Power Supply System Overview
2

## Slide 3: Distribution of Power Supplies in Service Area
3

## Slide 4
4

## Slide 5: OVERVIEW OF STORAGE RING POWER SUPPLIES
5
MAGNET | QUANTITY |  | Nº PS | SPARE | Current (A) | Voltage (V) | OUTPUT POWER (kW)
DIPOLES | 33 |  | 1 | 0 | 600 | 750 | 450
QUADRUPOLES | 112 | 16 (Q200) | 88 | 8 | 200 | 15 | 3
 |  | 48 (Q260) |  |  |  |  | 
 |  | 24 (Q280) |  |  |  |  | 
 |  | 24 (Q500) | 24 | 2 | 225 | 25 | 5,625
SEXTUPOLES | 120 | 4 families x 8 magnets (S150A) | 4 | 1 | 215 | 100 | 21,5
 |  | 2 families x 16 magnets (S150B) | 2 | 0 | 215 | 190 | 40,85
 |  | 2 families x 24 magnets (S220A) | 2 | 1 | 215 | 350 | 75,25
 |  | 1 family x 8 magnets (S220B) | 1 | 0 | 215 | 125 | 26,875
CORRECTORS | 208 | Horizontal | 88 | 6 | ±12 | ±60 | 200
 |  | Vertical | 88 | 6 | ±12 | ±60 | 200
 |  | Skew | 2 | 0 | ±5 | ±60 | 200

## Slide 6: OVERVIEW OF BOOSTER POWER SUPPLIES
MAGNET | QUANTITY |  | Nº PS | SPARE | Current (Apeak) | Voltage (Vpeak) | OUTPUT ACTIVE POWER (kW)
DIPOLES | 40 | 40 coils | 1 | 0 | 750 | ±1000 | 95
 |  | 40 coils | 1 | 0 | 750 | ±1000 | 95
QUADRUPOLES | 60 | 16 (series connection 8+8) | 2 | 0 | 180 | ±100 | 3,5
 |  | 8 | 1 | 0 | 180 | ±200 | 5,6
 |  | 36 | 1 | 0 | 180 | ±750 | 24,5
SEXTUPOLES | 16 (series connection 8+8) |  | 2 | 0 | ±8 | ±60 | 0,45
CORRECTORS | 72 |  | 72 | 4 | ±6 | ±10 | 0,25

## Slide 7: OVERVIEW OF TRANSFER LINES POWER SUPPLIES
MAGNET | QUANTITY |  | Nº PS | SPARE | Current (A) | Voltage (V) | OUTPUT POWER (W)
DIPOLES | 2 | type 1 | 1 | 0 | 180 | 20 | 3600
 |  | type 2 | 1 | 0 | 12 | 12 | 150
QUADRUPOLES | 9 |  | 9 | 1 | 15 | 20 | 300
CORRECTORS | 8 |  | 8 | 2 | ±2 | ±2 | 4
LINAC to BOOSTER TL
BOOSTER to STORAGE RING TL
MAGNET | QUANTITY | Nº PS | SPARE | Current (A) | Voltage (V) | OUTPUT POWER (W)
DIPOLES | 2 | 2 | 0 | 180 | 60 | 10800
QUADRUPOLES | 7 | 7 | 1 | 170 | 15 | 2500
CORRECTORS | 8 | 8 | 2 | ±6 | ±10 | 60

## Slide 8: Procurement of Power Supplies
Call for tenders for different subsystems (Transfer lines, Booster, Storage Ring)
Turnkey approach.
3 Companies
Bruker (Now Sigmaphi Electronics) for Transfer Lines and Booster
Hazemayer for SR Dipole, Sextupoles and Quadrupoles
OCEM – Storage Ring Correctors

## Slide 9: Today’s Solutions are Tomorrow’s Problems
Yesterday’s Solutions:
Transfer the risk of a new design to an external company
Low Manpower needed, only to follow up the companies
Low delivery time.
Today’s Problems
Risk of out of business of a manufacturer.
Companies may change their business.
The complete know how is in the manufacturer.
Design errors that appear after long term in operation. Not cover by warranties.

## Slide 10: SAT , Installation and Commissioning (2009-10)
All Power were tested before installation in SA
Exception:
Booster Bending and Quadrupoles
Storage Ring Bending Power Supplies
Storage Ring Sextupoles Power Supplies

## Slide 11: Stability Test Results

## Slide 12: Commissioning
Serious incidents with Booster Dipole Power Supplies During Commissioning
Lesson Learnt: The commissioning of Large Power Supplies could be long and painful. Take time and do not rush into the commissioning of other subsystems.

## Slide 13: Commissioning of Storage Ring Power Supplies
111 out of 112 Storage Ring Quadrupoles Connected with the wrong polarity.
Lesson Learn: Polarity meaning may change according to different specialist.
16 March 2010: Beam Accumulated
Acummulation
1.5 mA stored

## Slide 14: Electronics Section
Composed by
  8 electronics engineers
  6 electronics technicians

## Slide 15: Electronics Section Functions
  Control Hardware (cPCI, DIO cards, NIM...)
  Accelerator Power Supplies
  Instrumentation support (ADCs, DACs, Counters, V2F,...)
  Motion control (ICEPAP project)
  Timing System
  Centralized Hardware Documentation Repository (CableDB)
  Hardware installation
  Electronics design projects

## Slide 16: Tools for Operation
On-Call system: 1 Engineer and 1 technician 24 Hs during operation
Incident Management
Incident Register
Cable Database
Request Tracker (RT) migrating to JIRA
Elog
Weekly Power Supply meeting (1 hr)
Weekly Electronics Section Meeting ( 1Hr )

## Slide 17: Once in Lifetime Incidents
2013 - Water Leakage in Booster Bending and LT Power Supplies.

## Slide 18: Once in Lifetime Incidents
2013 - Water Leakage in Booster Bending and LT Power Supplies.

## Slide 19: Once in Lifetime Incidents
Auxiliary Power Supplies in SR-QUAD.
Several PS were not operative after shutdown period.

## Slide 20: Some Operation Statistics

## Slide 26: Today’s main concern
Booster Dipole Power Supplies:
Two Main Problems
1) very low lifetime of 2Q modules under the stress of top-up operation.
Power and thermal cycling.
2) Large difficulties to make failure diagnostics when the control/regulation boards are involve.

## Slide 27: Problem Solving Approaches:
First step. More spare modules are needed in order to reduce the risks.
Further steps:
Under evaluation.
refurbish the 2Q modules:
over-dimension IGBT
SiC modules
2) We must have a control/regulation boards with a complete access (documentation, firmware, etc)

## Slide 28: Thank you Questions Suggestions?