## Slide 1: New active filter for COSY dipole power converter
May 29, 2016 | Markus Retzlaff & Christian Ehrlich
Many thanks for the support of the IKP-4 Members, FZJ BoD and the HGF Members

## Slide 2: Summery
Power converter overview
Interaction between thyristor- & parallel feeding- stage
Development steps for the new parallel feeding, by Markus Retzlaff & Christian Ehrlich
Development of the new transistor driver, by Christian Ehrlich
Development of the new linear stage, by Markus Retzlaff

## Slide 3: Power converter overview
control cabinet thyristor cabinet parallel feeding
2600 x 2200 x 850 mm 5200 x 2200 x 1200 mm 3000 x 2200 x 900 mm

## Slide 4: Power converter overview
Thyrister
stage
Parallel feeding
COSY dipole magnets 24 (25)
output current 5000 A (20ppm), output voltage 1250 V, 6.25 MW

## Slide 5
Power converter overview
Interaction between thyristor- & parallel feeding- stage
Development steps for the new parallel feeding, by Markus Retzlaff & Christian Ehrlich
Development of the new transistor driver, by Christian Ehrlich
Development of the new linear stage, by Markus Retzlaff

## Slide 6: Interaction between thyristor- & parallel feeding- stage
Main Current
IM = IS + IP
Thyristor Current
IS
Prallel feeding Current
IP

## Slide 7
Power converter overview
Interaction between thyristor- & parallel feeding- stage
Development steps for the new parallel feeding, by Markus Retzlaff & Christian Ehrlich
Development of the new transistor driver, by Christian Ehrlich
Development of the new linear stage, by Markus Retzlaff

## Slide 8: Development steps for the new parallel feeding
New active filter structure
Extension for the new linear stage
New transistor gate driver
New linear stage
by Christian Ehrlich
by Markus Retzlaff

## Slide 9
Power converter overview
Interaction between thyristor- & parallel feeding- stage
Development steps for the new parallel feeding, by Markus Retzlaff & Christian Ehrlich
Development of the new transistor driver, by Christian Ehrlich
Development of the new linear stage, by Markus Retzlaff

## Slide 10: The old transistor driver from 1988
Four versions: 029.105.454 (switch stage „oben“), 029.105.546 (switch stage „unten“), 029.105.458 (analog stage „oben“), 029.105.460 (analog stage „unten“)

## Slide 11: The new transistor driver
One Mainboard for all versions. Setting with selector switch

## Slide 12: Global pcb setting indicator & switch
PCB setting switch (one Mainboard for all four old versions)
PCB setting idicator

## Slide 13: Single pcb setting idicator, „OK“

## Slide 14: Single pcb setting idicator, „wrong“

## Slide 15: Major functions
The new transistor driver must have the same seven major functions:
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor monitoring
Reset driver
Transistor gate driver (BUZ45)
Logic for interlocks

## Slide 16: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 17: Voltage monitor
Status display
Measuring points

## Slide 18: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 19: Grid synchronisation
20ms
10ms
10ms
warning
normal operation

## Slide 20: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 21: Fiber optic communication
Testpoints
LWL
10ms = normal operation
20ms = warning
> 20ms = shutdown

## Slide 22: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 23: Input ports and MiniSemi monitoring
Version „unten“ (down)
MiniSemi for the intermediate circuit

## Slide 24: Output ports
Version „oben“ (up)
Shutdown output
Warning output
LWL
Transistor gate driver „unten“
Transistor gate driver „oben“
wire
warning
shutdown

## Slide 25: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 26: Transistor gate driver
Gate connection to 384 BUZ45 transistors

## Slide 27: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 28: Transistor monitoring
One of the transistor holders
384 BUZ45 Transistors
128 transistor groups (6 in each group)
warning =
1 group failure
shutdown =
3 groups failure
1750 mm
1100 mm

## Slide 29: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 30: Reset driver
Single transistor group monitoring
error memory

## Slide 31: Module functions
Voltage monitoring
Grid synchronisation
Fiber optic communication
IO-Ports
Transistor gate driver (BUZ45)
Transistor monitoring
Reset driver
Logic for interlocks

## Slide 32: Logic for interlocks, „oben“ & „unten“
Every signal on testpoints
No software used, only gatter logic

## Slide 33: Logic for interlocks, version „unten“
Every signal on testpoints
No software used, only gatter logic
Error memory
with LED

## Slide 34: Logic for interlocks, version „oben“
Every signal on testpoints
No software used, only gatter logic
Error memory
with LED

## Slide 35: Old mainboard had to be calibrated after repair, in case of an error

## Slide 36: The new mainboard is balanced in itself, by calibration of the function modules

## Slide 37: Every spare parts are calibrated with the external testing bench
Resistors for calibration

## Slide 38: Repair without special knowledge about the dipol power converter is possible
defect pcb out
tested pcb in

## Slide 39: Maintenance time is much shorter
All terminals of the mainboard are pluggable
All function blocks are modular
All spare parts are calibrated
One mainboard for all four old versions
„siri-function“ for PCB setting control
All important signals are fed directly to LEMO sockets or test points
Compatible with old upper boards E1-E3
No special knowledge of the activ filter required, all components are coded and clearly labeled

## Slide 40: Necessary modifications and difficulties in developing
Current connection must be changed to terminal blocks
No further mechanical work necessary, because the entire mechanism and terminal positioning is equal to the old version
Difficulties during planning and development:
Measuring of the dipol electronics only during maintenance possible
Incomplete documentation
Subtle differences in the old version
Handmade connections on the old pcb

## Slide 41
Power converter overview
Interaction between thyristor- & parallel feeding- stage
Development steps for the new parallel feeding, by Markus Retzlaff & Christian Ehrlich
Development of the new transistor driver, by Christian Ehrlich
Development of the new linear stage, by Markus Retzlaff

## Slide 42: Interface for the new linear stage
Same connection from the mainboard to the interface

## Slide 43: Interface for the new linear stage
Same Reset- and Transistormonitoring signals

## Slide 44: The old linear stage
MOSFETS are connected in parallel, with drain resistors.
No controlled symmetry, so we have to rely on the symmetery of the transistors themselfs
Groups of six transistors are supervized, to detect drifts or broken ones
Modern versions of the MOSFETs (BUZ45A) have enormous drifts, so we cannot use them in parallel connection. Or we have to select them with great discard.

## Slide 45: The new linear stage
Each MOSFET has ist own regulation, for better symmetry
Each MOSFET has ist own failure detection
MOSFET from IXYS specially designed for linear regulation
SOT-227 case instead of TO-3

## Slide 46: The new linear stage
Easy daisy chain connection of the regulation boards with FFC and bus bars

## Slide 47: Outlook for the linear stage
In the future, the intermediate circuit will be dynamic, instead of the static system from now. This would dramatically reduce the power loss of the linear stage, and we can also reduce the number of transistors.
This will be realized with a source- / sink power converter, to be able, to feed the energy back into the mains, during discharging the magnets.

## Slide 48
Thanks for your attention